## FIT_Hours_Year
Author Daniel Gumy | Date 15.02.2013
Blue colored Values can be over written. The equivalent values are found on the same line.
| FIT | Hours | Years | Days
| 1175 | 851063.8298 | 97.1534 | 35460.9929
| 2003.16 | 499211.2462 | 56.9876 | 20800.4686
| 1000 | 1000000 | 114.1553 | 41666.6667
| FIT | Hours | Years | Days
| 1176.4706 | 850000 | 97.032 | 35416.6667
| 1000 | 1000000 | 114.1553 | 41666.6667
| 10000 | 100000 | 11.4155 | 4166.6667
| FIT | Hours | Years | Days
| 1176.4706 | 850000 | 97.032 | 35416.6667
| 3469.7645 | 288204 | 32.9 | 12008.5
| 1141.5525 | 876000 | 100 | 36500

## FFR PCD1_2 Calculator
|  |  | Example for a Typical Configuration |  |  |  |  | Availability: |  | Real configuration to be filled by the User |  |  |  |  | Availability
Type / Field Failure Rate [FFR] |  |  |  | 1/FFR | Summ | FFR Total |  |  |  |  | 1 / FFR | Summ | FFR Total
| [mio h] | [Years
PCD1, PCD2 |  | @ 24h/D] |  |  | 0.064571 | 15.4867 | 135663.7168 | 100% |  |  |  | 0.074117 | 13.4923 | 118192.1227 | 100%
C100, C150 | 8.76 | 1000 | 1 | 0.001 | [5 empty] | 1 | 0.001
C2000 | 8.76 | 1000 | 0 | 0 | [5 empty] | 0 | 0
M110, 120, M150 | 0.6132 | 70 | 0 | 0 | [5 empty] | 1 | 0.014286
M17x, M48x | 0.5256 | 60 | 1 | 0.016667 | [5 empty] | 0 | 0
M5xxx 1) | 0.1752 | 20 | 0 | 0 | [5 empty] | 0 | 0
E11x, E16x, E61x | 4.38 | 500 | 3 | 0.006 | [5 empty] | 0 | 0
A200,220,250 3) | 3.504 | 400 | 1 | 0.0025 | [5 empty] | 0 | 0
A300, A400, A46x | 6.132 | 700 | 6 | 0.0085714 | [5 empty] | 0 | 0
W1xx | 1.752 | 200 | 0 | 0 | [5 empty] | 3 | 0.015
W2, W3, W4, W6 | 3.504 | 400 | 1 | 0.0025 | [5 empty] | 0 | 0
W5 | 2.628 | 300 | 1 | 0.0033333 | [5 empty] | 0 | 0
H1 | 3.504 | 400 | 0 | 0 | [5 empty] | 1 | 0.0025
R6000 | 2.628 | 300 | 0 | 0 | [5 empty] | 0 | 0
F2xxx | 2.628 | 300 | 0 | 0 | [5 empty] | 0 | 0
F5xx | 2.628 | 300 | 0 | 0 | [5 empty] | 0 | 0
T8 1) PCD7 | 1.752 | 200 | 0 | 0 | [5 empty] | 0 | 0
F1xx, F2xx | 8.76 | 1000 | 2 | 0.002 | [5 empty] | 2 | 0.002
F6xx, F7xx, F8xx | 0.876 | 100 | 1 | 0.01 | [5 empty] | 1 | 0.01
F74xx | 1.752 | 200 | 1 | 0.005 | [5 empty] | 1 | 0.005
F75xx | 1.752 | 200 | 1 | 0.005 | [5 empty] | 0 | 0
R4xx | 8.76 | 1000 | 1 | 0.001 | [5 empty] | 0 | 0
R5xx | 8.76 | 1000 | 1 | 0.001 | [5 empty] | 0 | 0
H104S 1) | 1.752 | 200 | 0 | 0 | [5 empty] | 0 | 0
D23x | 0.7884 | 90 | 0 | 0 | [5 empty] | 0 | 0
D4xx 1) 2) 5) | 0.36004 | 41.1 | 0 | 0 | [5 empty] | 1 | 0.024331
PCS1.Cxx 1) | 0.3504 | 40 | 0 | 0 | [5 empty] | 0 | 0
1) Previsional estimation | [8 empty] | 0
2) Backlight: 50% luminosity after 50'000h 5) PCD7.D457VTSF: 2775. FIT, 360'326 h, 15014 T, 41.1 Jahre @65°C
3) Subject to limited Life Time; for Relais typical 0.7 x 106 cycles
Field Failure Rate [FFR] is practically equivalent to the MTBF(Mean Time Between Failure), in million of Hours and year at 24 hours a day, 7 days a week. These FFR are gross. There are defined as the ration between the Cumulative producted Modules multiplied by Time and the number of modules returned to Murten for Repair, regardless whether the module is defective or not, if the user has made a mistake or not.
Availibility=FFR / (FFR + Rtime) Availability is based on - the condition where the customer is supposed to have spare modules - so an estimated 'Repair time' of 4 hours to localize and replaced the defective module can be applied.

## FFR PCD3 Calculator
|  |  | Example for a Typical Configuration |  |  |  |  | Availability: | Real configuration to be filled by the User |  |  |  |  | Availability
Type / Field Failure Rate [FFR] |  |  |  | 1/FFR | Summ | FFR Total |  |  |  | 1 / FFR | Summ | FFR Total
| [mio h] | [Years
PCD3 |  | @ 24h/D] |  |  | 0.031806 | 31.4408 | 275421.7722 | 100% |  |  | 0.033472 | 29.8753 | 261707.9106 | 100%
C100, C110 | 8.76 | 1000 | 1 | 0.001 |  |  |  |  | 0 | 0
C200 | 3.504 | 400 | 0 | 0 |  |  |  |  | 0 | 0
M3xxx, M5xxx 4) M6xxx @35°C | 0.8506 | 97.1 | 0 | 0 |  |  |  |  | 0 | 0
M3xxx, M5xxx 4) M6xxx @50°C | 0.49932 | 57 | 1 | 0.017544 |  |  |  |  | 1 | 0.017544
M3xxx, M5xxx 4) M6xxx @65°C | 0.2882 | 32.9 | 0 | 0 |  |  |  |  | 0 | 0
T66x 1) | 0.1752 | 20 | 0 | 0 |  |  |  |  | 0 | 0
T76x 1) | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
E11x, E16x, E61x | 4.38 | 500 | 3 | 0.006 |  |  |  |  | 1 | 0.002
A200,220,250 3) | 3.504 | 400 | 1 | 0.0025 |  |  |  |  | 2 | 0.005
A300, A400, A46x | 6.132 | 700 | 1 | 0.0014286 |  |  |  |  | 1 | 0.0014286
W1xx | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
W2, W3, W4, W6 | 3.504 | 400 | 0 | 0 |  |  |  |  | 3 | 0.0075
W5 | 2.628 | 300 | 1 | 0.0033333 |  |  |  |  | 0 | 0
H1 | 3.504 | 400 | 0 | 0 |  |  |  |  | 0 | 0
R5xx, R6xx 1) | 2.628 | 300 | 0 | 0 |  |  |  |  | 0 | 0
F1xx | 2.628 | 300 | 0 | 0 |  |  |  |  | 0 | 0
F2xx | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
PCD7
F1xx | 8.76 | 1000 | 0 | 0 |  |  |  |  | 0 | 0
R-SD xxx | 0.9636 | 110 | 0 | 0 |  |  |  |  | 0 | 0
D4xx 1) 2) 5) | 0.36004 | 41.1 | 1 | 0.024331 |  |  |  |  | 0 | 0
1) Previsional estimation
2) Backlight: 50% luminosity after 50'000h 5) PCD7.D457VTSF: 115.1Years @35°C, 70.9Years @50°C, 21.6Years @65°C
3) Subject to limited Life Time; for Relais typical 0.7 x 106 cycles
4) MTBF calculated: 38.1Years @35°C, 29.9Years @50°C, 21.6Years @65°C,
Field Failure Rate [FFR] is practically equivalent to the MTBF(Mean Time Between Failure), in million of Hours and year at 24 hours a day, 7 days a week. These FFR are gross. There are defined as the ration between the Cumulative producted Modules multiplied by Time and the number of modules returned to Murten for Repair, regardless whether the module is defective or not, if the user has made a mistake or not.
Availibility=FFR / (FFR + Rtime) Availability is based on - the condition where the customer is supposed to have spare modules - so an estimated 'Repair time' of 4 hours to localize and replaced the defective module can be applied.
How to interpret the value of MTBF? After a Time of one MTBF all sample of a population has to be repaired and put again into service. = if you have 100 or 1000x PCD3.M90 in service, after 31.4 years all 100 or 1000 failed once. =during a time slice of 10 years the percentage of once failed devices is: 100% * Time duration / MTBF 100%* 10 years/ 31.4= 31.8% In the practice: - higher failures rate happened during the first year due to additional stress provoked by all manual interventions, and also in a smaller part due to the early mortality of components. - good environment lowers the defective rate through lower and constant temperature and humidity, clean atmosphere, infrequent human intervention, etc. ... .

## FFR PCD3M90 Calculator
|  |  | Example for a Typical Configuration |  |  |  |  | Availability: | Real configuration to be filled by the User |  |  |  |  | Availability
Type / Field Failure Rate [FFR] |  |  |  | 1/FFR | Summ | FFR Total |  |  |  | 1 / FFR | Summ | FFR Total
| [mio h] | [Years
PCD3 |  | @ 24h/D] |  |  | 0.031806 | 31.4408 | 275421.7722 | 100% |  |  | 0.033472 | 29.8753 | 261707.9106 | 100%
C100, C110 | 8.76 | 1000 | 1 | 0.001 |  |  |  |  | 0 | 0
C200 | 3.504 | 400 | 0 | 0 |  |  |  |  | 0 | 0
M3xxx, M5xxx 4) M6xxx @35°C | 0.8506 | 97.1 | 0 | 0 |  |  |  |  | 0 | 0
M3xxx, M5xxx 4) M6xxx @50°C | 0.49932 | 57 | 1 | 0.017544 |  |  |  |  | 1 | 0.017544
M3xxx, M5xxx 4) M6xxx @65°C | 0.2882 | 32.9 | 0 | 0 |  |  |  |  | 0 | 0
T66x 1) | 0.1752 | 20 | 0 | 0 |  |  |  |  | 0 | 0
T76x 1) | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
E11x, E16x, E61x | 4.38 | 500 | 3 | 0.006 |  |  |  |  | 1 | 0.002
A200,220,250 3) | 3.504 | 400 | 1 | 0.0025 |  |  |  |  | 2 | 0.005
A300, A400, A46x | 6.132 | 700 | 1 | 0.0014286 |  |  |  |  | 1 | 0.0014286
W1xx | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
W2, W3, W4, W6 | 3.504 | 400 | 0 | 0 |  |  |  |  | 3 | 0.0075
W5 | 2.628 | 300 | 1 | 0.0033333 |  |  |  |  | 0 | 0
H1 | 3.504 | 400 | 0 | 0 |  |  |  |  | 0 | 0
R5xx, R6xx 1) | 2.628 | 300 | 0 | 0 |  |  |  |  | 0 | 0
F1xx | 2.628 | 300 | 0 | 0 |  |  |  |  | 0 | 0
F2xx | 1.752 | 200 | 0 | 0 |  |  |  |  | 0 | 0
PCD7
F1xx | 8.76 | 1000 | 0 | 0 |  |  |  |  | 0 | 0
R-SD xxx | 0.9636 | 110 | 0 | 0 |  |  |  |  | 0 | 0
D4xx 1) 2) 5) | 0.36004 | 41.1 | 1 | 0.024331 |  |  |  |  | 0 | 0
1) Previsional estimation
2) Backlight: 50% luminosity after 50'000h 5) PCD7.D457VTSF: 115.1Years @35°C, 70.9Years @50°C, 21.6Years @65°C
3) Subject to limited Life Time; for Relais typical 0.7 x 106 cycles
4) MTBF calculated: 38.1Years @35°C, 29.9Years @50°C, 21.6Years @65°C,
Field Failure Rate [FFR] is practically equivalent to the MTBF(Mean Time Between Failure), in million of Hours and year at 24 hours a day, 7 days a week. These FFR are gross. There are defined as the ration between the Cumulative producted Modules multiplied by Time and the number of modules returned to Murten for Repair, regardless whether the module is defective or not, if the user has made a mistake or not.
Availibility=FFR / (FFR + Rtime) Availability is based on - the condition where the customer is supposed to have spare modules - so an estimated 'Repair time' of 4 hours to localize and replaced the defective module can be applied.
Chose in function of operating temperature 35°C 50°C 65°C
Equivalent I/O for PCD3.M90

## FFR PCD7_D Calculator
|  |  | Example for a Typical Configuration |  |  |  |  | Availability: |  | Real configuration to be filled by the User |  |  |  |  | Availability
Type / Field Failure Rate [FFR] |  |  |  | 1/FFR | Summ | FFR Total |  |  |  |  | 1 / FFR | Summ | FFR Total
| [mio h] | [Years
PCD7.Dxxx, PCS1 |  | @ 24h/D] |  |  | 0.0086881 | 115.1 | 1008276 | 100% |  |  |  | 0.0086881 | 115.1 | 1008276 | 100%
D23x | 0.7884 | 90 | 0 | 0 | [5 empty] | 0 | 0
D4xx 1) 2) 5) @35°C | 1.0083 | 115.1 | 1 | 0.0086881 | [5 empty] | 1 | 0.0086881
D4xx 1) 2) 5) @50°C | 0.62108 | 70.9 | 0 | 0 | [5 empty] | 0 | 0
D4xx 1) 2) 5) @65°C | 0.36004 | 41.1 | 0 | 0 | [5 empty] | 0 | 0
PCS1.Cxx 1) | 0.3504 | 40 | 0 | 0 | [5 empty] | 0 | 0
1) Previsional estimation | [8 empty] | 0
2) Backlight: 50% luminosity after 50'000h 5) PCD7.D457VTSF: 2775. FIT, 360'326 h, 15014 T, 41.1 Jahre @65°C
3) Subject to limited Life Time; for Relais typical 0.7 x 106 cycles
Field Failure Rate [FFR] is practically equivalent to the MTBF(Mean Time Between Failure), in million of Hours and year at 24 hours a day, 7 days a week. These FFR are gross. There are defined as the ration between the Cumulative producted Modules multiplied by Time and the number of modules returned to Murten for Repair, regardless whether the module is defective or not, if the user has made a mistake or not.
Availibility=FFR / (FFR + Rtime) Availability is based on - the condition where the customer is supposed to have spare modules - so an estimated 'Repair time' of 4 hours to localize and replaced the defective module can be applied.