## Slide 1: Ether-S-Bus communication between 2 PCD’s
December 1st, 2006

## Slide 2: Ether-S-Bus communication between 2 PCD’s
Content
1. How connect 2 PCD’s together ???
2. What to configure at first ???
3. Define a SLAVE station
4. Define a MASTER station
5. Communication MASTER to SLAVE ???
  5.1 How to SEND data ???
  5.2 How to RECEIVE data ???
6. Communication MASTER to MASTER ???
7. Test
8. Contact us

## Slide 3: 1. How connect 2 PCD’s together ???
1 crossed Ethernet cable (1st possibility)
Switch
Station 1
(PCD)
Station 2
(PCD)
1 Switch and 2 direct Ethernet cables (2nd possibility)
2 possibilities:
crossed ethernet cable
direct ethernet cable
direct ethernet cable
Q.NET-5TX
PCD3.Mxxxx
PCD3.Mxxxx

## Slide 4: 2. What to configure at first ???
Station 1
Station 2
Sbus station number/address
IP address ( + Mask + default Gateway)
Network parameters ( Device Configurator in PG5 2.0):
IP Node
 Download the Configuration
(Device Configurator in PG5 2.0)
 Now the Station 1 is SLAVE
Sbus no: 45
IP addr. : 172.16.1.45
IP Node: 45
Switch
SLAVE
SBus No: 45
IP node: 45
 Do the same for the Station 2
Sbus no: 46
IP addr. : 172.16.1.46
IP Node: 46
SLAVE
SBus No: 46
IP node: 46

## Slide 5: 3. Define a SLAVE station
Nothing have to be done
Configuration of “Network Parameters” are sufficient
(see section “2. What to configure at first ???”)
SLAVE: (on Station 2 )
Sbus no: 45
IP addr. : 172.16.1.45
IP Node: 45
Sbus no: 46
IP addr. : 172.16.1.46
IP Node: 46
Switch
SLAVE
(Station 1)
SBus No: 45
IP node: 45
SLAVE
(Station 2)
SBus No: 46
IP node: 46

## Slide 6: 4. Define a MASTER station
Create à “FUPLA” file
Add “SASI Sbus IP Master” Fbox
MASTER: (for example on Station 1)
Give him a “Name” (for example Master_1)
Set the correct “Channel”
(available on the Ethernet Interface of the PCD3.Mxxxx)
 Now the Station 1 is defined as MASTER
SLAVE
(Station 1)
SBus No: 45
IP node: 45
Switch
SLAVE
(Station 2)
SBus No: 46
IP node: 46
MASTER
(Station 1)
SBus No: 45
IP node: 45
“Build all” + “Download”

## Slide 7: 5. Communication MASTER to SLAVE ???
Switch
SLAVE
(Station 2)
SBus No: 46
IP node: 46
MASTER
(Station 1)
SBus No: 45
IP node: 45
Ether-S-Net network
Fbox’s to use: (in the MASTER station)
“SASI Sbus MASTER”
“SEND” FBox
“RCV” FBox
R 0
R 10
SEND (write)
R 1
R 11
RECEIVE (read)
RESSOURCE
RESSOURCE
MASTER
(Station 1)
SBus No: 45
IP node: 45

## Slide 8: 5.1. How to SEND data ???
Switch
SLAVE
(Station 2)
SBus No: 46
IP node: 46
MASTER
(Station 1)
SBus No: 45
IP node: 45
R 0
R 10
Ether-S-Net network
SEND (write)
RESSOURCE
RESSOURCE
In MASTER station/
In the same Fupla file
“SEND” Fbox:
MASTER
(Station 1)
SBus No: 45
IP node: 45

## Slide 9: 5.2 How to RECEIVE data ???
Switch
SLAVE
(Station 2)
SBus No: 46
IP node: 46
MASTER
(Station 1)
SBus No: 45
IP node: 45
R 1
R 11
Ether-S-Net network
RECEIVE (read)
RESSOURCE
RESSOURCE
In MASTER station/
In the same Fupla file
“RCV” Fbox
MASTER
(Station 1)
SBus No: 45
IP node: 45

## Slide 10: 6. Communication MASTER to MASTER ???
Switch
SLAVE
(Station 2)
SBus No: 46
IP node: 46
MASTER 1
(Station 1)
SBus No: 45
IP node: 45
Ether-S-Net network
R 0
R 10
SEND
R 1
R 11
RECEIVE
RESSOURCE
RESSOURCE
R 20
R 30
SEND
R 21
R 31
RECEIVE
Add:
“SEND” FBox
Add:
“RCV” FBox
2ND MASTER station:
(see section 4:
“4. Define a MASTER station”)
MASTER 2
(Station 2)
SBus No: 46
IP node: 46
(see section 5.1)
(see section 5.2)
Define Station 2
as MASTER

## Slide 11: 7. Test
End of this QUICK START
Test you program
Test:
direct ethernet cable
direct ethernet cable
Q.NET-5TX
PCD3.Mxxxx
PCD3.Mxxxx

## Slide 12: 8. Contact us
Saia-Burgess Controls AG
Rue de la Gare 18
CH-3280 Morat
Switzerland
Technical Support
  Phone: 026 / 672 71 11
  Fax: 026 / 672 74 99
  Website: www.sbc-support.ch
  E-mail : pcdsupport@saia-burgess.com